## Instruction Sheet
Steam Trap Repair User Guide
Purpose: | This spreadsheet calculates the energy, cost and emissions savings from repairing broken steam traps connected to a condensate return. Payback and other values of the system are also reported.
How to use the spreadsheet | 1 | Enter Required Data in Input Fields: Populate the designated white cells in each section with facility and steam system information.
| 2 | Review Summary Results: Refer to the Summary and Calculated Data sections for an overview of key metrics, including annual energy savings, cost savings, CO₂ reduction, and the simple payback period. This section provides a high-level assessment of the financial and environmental benefits of repairing steam traps.
| 3 | Consult Calculation Notes and Assumptions for Methodology: For a thorough understanding of the underlying calculations, refer to the Calculation Procedures and Notes section. This section contains variable definitions, assumptions, and formulas used in the analysis, offering valuable context and transparency.
Section Overview and Input Instructions
Facility and Procedure Information | Client Information | This section allows you to input general project details, such as the client name, location, and assessment date. While optional, this information helps maintain organized records for each assessment.
| Facility Information | Enter data about the facility, including CO2 emission factor and cost .
Calculation Procedures and Notes | Variable Table | This table provides a comprehensive list of variables used in the analysis, along with units and descriptions for each. It serves as a reference to help users understand the specific parameters applied in each calculation.
| Assumptions | These are assumptions made to allow for the calculations used in the spreadsheet. Ensure that these assumptions are acceptable for your system before using this spreadsheet
| Formulas | Outlines the formulas used in calculating steam loss, energy savings, and cost savings etc. This section allows users to understand the methodology used in the claculations for the spreadsheet.
Results | Calculated Data | Provides calculated values regarding the facility steam system
| Cost Analysis | Provides economic indicators that will be used in the recommendation report
Summary |  | Presents an overview of key outcomes, including total annual energy savings, CO₂ emission reduction, and payback period. This section highlights the financial and environmental benefits of repairing steam traps.
This tool is based upon work supported by the U.S. Department of Energy’s Office of Manufacturing and Energy Supply Chains (MESC Award Number DE-MS0000022). The views expressed herein do not necessarily represent the views of the U.S. Department of Energy or the United States Government.
This tool was created to provide estimates of savings and costs that serve as helpful information. This tool does not guarantee that no variation will exist between the calculated costs and savings and real market costs and savings. The spreadsheet is distributed locked so as to avoid unintentional altering of formulas, but can be unlocked by selecting the "unprotect sheet" option under the review tab. There is no password.

## Steam Traps
Steam Trap Repair
AR Code: 2.2113.2
Collected Data
Enter AR-specific information into white cells
Client Information |  |  | Steam Traps |  |  |  |  | Facility Steam
Enter client-specific information into white cells |  |  | Enter values for individual steam traps |  |  |  |  | Enter values from the steam system
Client Information (optional) |  |  | Steam Traps | Orifice Diameter [in] | Pressure [psig] | Flow [lb/hr] |  | Saturated Vapor Enthalphy (Boiler) [btu/lb] | Saturated Liquid Enthalpy (condensate return) [btu/lb] | Enthalpy of Makeup Water [btu/lb] | Percent Feedwater From Makeup Water [decimal] | Combustion Efficiency [decimal] | Heating Value [btu/MCF]
IAC Assessment #: |  |  | Steam Trap 1 |  |  | 0
Client Name: |  |  | Steam Trap 2 |  |  | 0
Location: |  |  | Steam Trap 3 |  |  | 0
ZIP code: |  |  | Steam Trap 4 |  |  | 0 |  | Assumptions Implicit in Calculations
SIC: |  |  | Steam Trap 5 |  |  | 0 |  | Condensate is returned to the boiler via condensate return lines
NAICS: |  |  | Steam Trap 6 |  |  | 0 |  |  | If NOT true, use Steam Leak AR
Assessment Date: |  |  | Steam Trap 7 |  |  | 0 |  | Napier Formula used to calculate steam flow through trap orifice
|  |  | Steam Trap 8 |  |  | 0 |  |  | Different approaches can be found at TLV and Armstrong int.
Facility Information | Value | Units | Steam Trap 9 |  |  | 0
CO2 Emission Factor |  | tons/MMBtu | Steam Trap 10 |  |  | 0
Operating hours |  | hr/yr | Steam Trap 11 |  |  | 0
Volumetric Fuel Cost |  | $/MCF | Steam Trap 12 |  |  | 0
Labor Rate |  | $/hr | Steam Trap 13 |  |  | 0
Repair Time |  | hr/trap | Steam Trap 14 |  |  | 0
Cost of Steam Traps |  | $/trap | Steam Trap 15 |  |  | 0
|  |  | Total | - | - | 0
Summary
|  |  | Calculated Data |  |  |  | Cost Analysis
Savings, costs, and other variables are calculated below |  |  | Values calculated from provided data |  |  |  | Implementation cost, and payback are calculated below
Calculated Variables | Value | Units | Energy to Boil Feedwater [MMBtu/klb] | Fuel Cost [$/MMBtu] | Cost of Steam [$/klb steam] |  | Implementation Cost [$] | Payback [yr]
Annual Energy Savings | #DIV/0! | MMBTU/yr
Annual Energy Cost Savings | #DIV/0! | $/yr |  |  |  |  | 0 | #DIV/0!
Capital Cost | 0 | $ | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
CO2 Reduction | #DIV/0! | tons/yr
Simple Payback | #DIV/0! | yrs
Calculation Procedure and Notes
Important information for clients, formulas, and tables used to calculate results
|  |  | Variable Description |  | Variable | Average Value | Unit |  | Notes
|  |  | Number of Steam Traps |  | NT | 0 | Traps
|  |  | Orifice Diameter |  | DO | #DIV/0! | in
|  |  | Guage Pressure in Line |  | PPSIG | #DIV/0! | psig
|  |  | Total Steam Flow Through Broken Traps |  | FT | 0 | lb/hr
|  |  | Saturated Vapor Enthalpy in Boiler |  | hB | 0 | btu/lb
|  |  | Saturated Liquid Enthalpy in Condensate |  | hC | 0 | btu/lb
|  |  | Enthalpy of Makeup Water |  | hM | 0 | btu/lb
|  |  | Percent Feedwater from Makeup Water |  | XM | 0 | decimal
|  |  | Combustion Efficiency |  | ŋB | 0 | decimal
|  |  | Heating Value of Fuel |  | Hf | 0 | btu/MCF
|  |  | Energy to Boil Feedwater |  | QF | #DIV/0! | MMBtu/klb
|  |  | Fuel Cost |  | Cf | #DIV/0! | $/MMBtu
|  |  | Cost of Steam |  | CS | #DIV/0! | $/klb
|  |  | Implementation Cost |  | CI | 0 | $
|  |  | Payback |  | TP | #DIV/0! | yrs
|  |  | CO2 Emission Factor |  | GC02 | 0 | tons/MMBtu
|  |  | Operating hours |  | TO | 0 | hr/yr
|  |  | Volumetric Fuel Cost |  | CVF | 0 | $/MCF
|  |  | Labor Rate |  | CL | 0 | $/hr
|  |  | Repair Time |  | TR | 0 | hr/trap
|  |  | Cost of Steam Traps |  | CT | 0 | $/trap
|  |  | Annual Energy Savings |  | SE | #DIV/0! | MMBTU/yr
|  |  | Annual Energy Cost Savings |  | SC | #DIV/0! | $/yr
|  |  | CO2 Reduction |  | SCO2 | #DIV/0! | tons/yr
Formulas
Flow Through an Orifice (Napier Formula) = 24.24(Orifice Diameter)^2 (Absolute Pressure in Line)
Energy to Boil Feedwater = (1000lb)*((Sat. Vapor h - Sat. Liquid h) + (Feedwater from MU)*(Sat. Liquid h - h of MU))/(Boiler Efficiency)
Cost of Steam = (Fuel Cost) (Energy to Boil Feedwater)
Energy Savings = (Operating Hours)(Energy to Boil Feedwater)(Total Flow Through Broken Traps)/(1000lb)
Implementation Cost = (Number of Steam Traps) ((Labor Rate)(Repair Time) + (Cost of Steam Traps))
Payback Period = (Implementation Cost) / (Annual Energy Cost Savings)
𝑄𝑆=24.24(𝐷𝑂)2(𝑃𝑃𝑆𝐼𝐴)
𝐶𝑆=(𝐶𝐹)(𝑄𝐹)
𝑄_𝐹=(1000𝑙𝑏)((ℎ𝐵−ℎ𝐶)+(𝑋𝑀)(ℎ𝐶−ℎ𝑀))/ŋ𝐵
𝑆𝐸=(𝑇𝑂)(𝑄𝐹)(𝐹𝑇)/(1000𝑙𝑏)
𝑇𝑃=((𝐶𝐼))/((𝑆𝐸) )
𝐶𝐼=(𝑁𝑇)((𝐶𝐿)(𝑇𝑅)+𝐶𝑇)
Note on K9: Use steam tables at given temperatures and pressures for following enthalpies

## Cost Estimates
Cost Estimates
List of sources to suggest pricing options
Steam Traps |  |  | Labor Rates and
List of sources to suggest pricing options |  |  | List of sources to suggest pricing options
Cost Estimate ($) | Source | Updated | Cost Estimate ($) | Source | Updated
307 | https://www.walmart.com/ip/Spirax-Sarco-64150-B1H-125-12-CAST-IRON-INVERT-BUCKET-TRAP/2086580188?wmlspartner=wlpa&selectedSellerId=101353997&gQT=0&utm_source=Perplexity&utm_medium=referral | 2025-03-07 | 300-1000 (This is including labor and capital) | chrome-extension://efaidnbmnnnibpcajpcglclefindmkaj/https://www1.nationalgridus.com/files/AddedPDF/POA/20130828SteamTraps101.pdf | 2025-03-07
280 | https://www.bonanza.com/listings/Spirax-Sarco-FTI-15-66669-3-4-Float-And-Thermostatic-Steam-Trap-FTI15-Nsnp/1670992679?goog_pla=1&gQT=0&utm_source=Perplexity&utm_medium=referral | 2025-03-07
222 | https://www.nationalpumpsupply.com/404328-hoffman-b1030a-3-3-4-inverted-bucket-steam-trap-w-o-strainer/ | 2025-03-07